## Slide 1: Environmental Thermal Engineering
Lecture # 14
Min soo Kim
Mechanical & Aerospace Engineering

## Slide 2: Cooling Load

## Slide 3: Cooling Load
⊙ The amount of energy to be removed from space
to maintain constant temperature and humidity.
⊙ It is different to heat acquisition because solar heat coming through the
open space and radiation by the inner surface of wall and object
do not heat indoor air directly.
⊙ Decrease of maximum cooling load by thermal delay decide size of
air conditioner.

## Slide 4: Type of cooling load
Division |  | Contents | Type of heat
Indoor load | Solar radiation heat | ○ passing through the glass ○ passing through the wall(roof) contact with the outside air | Sensible Heat Sensible Heat
 | Conduction by thermal difference | ○ passing through the glass ○ passing through the wall(roof) contact with the outside air ○ passing through the mid-wall, floor and ceiling | Sensible Heat Sensible Heat Sensible Heat
 | Internally generated heat | ○ by lighting ○ by human body ○ by indoor facilities | Sensible Heat Sensible + Latent Sensible + Latent
 | Intrusion of outside air | ○ Air leakage of the window chassis and door crevice | Sensible + Latent
 | Others | ○ Heat loss at supply duct ○ Heat generation at ventilator | Sensible + Latent Sensible + Latent
Outdoor load | Introduction of outside air | ○ Calories to cool or humidify the outdoor air to indoor air | Sensible + Latent
Others |  | ○ Heat loss at supply duct, pipe ○ Heat generation at pump | Sensible + Latent

## Slide 5: Solar radiation heat
Heat gain and lose of building
They are affected by location of sun,
cleanliness of air, characteristic and direction
of building.
Amount of solar radiation
α + ρ + τ = 1
α : Absorption (The ratio of the absorption in total thermal radiation incident)
ρ : Reflectivity (The ratio of the reflection in total thermal radiation incident)
τ : Transmissivity (The ratio of the trajection in total thermal radiation incident)

## Slide 6: The solar data of each month(21th)
Month | Equation of Time(min) | Declination(degree)
January | 11.2 | -20.0
February | -13.9 | -10.8
March | -7.5 | 0.0
April | 1.1 | 11.6
May | 3.3 | 20.0
June | -1.4 | 23.45
July | -6.2 | 20.6
August | -2.4 | 12.3
September | 7.5 | 0.0
October | 15.4 | -10.5
November | 13.8 | -19.8
December | 1.6 | -23.45
Local solar time(LST) = Local civil time(LCT) + Equation of time(EOT)

## Slide 7: Solar heat gain by well-lighted surface
Well-lighted surface
- All outside surface of building that transmit sunlight
ex) Glass, Exterior/Interior shade devices
Total heat gain = Sunlight gain + Conduction gain
Conduction gain = Total heat transfer coefficient of lighted surface
* temperature difference between indoor/outdoor

## Slide 8
# Solar radiation projected into Glass
Incoming solar
Radiation (100%)
Inward flow of absorbed radiation(4%)
Transmitted solar radiation(80%)
Reflected radiation(8%)
Outward flow of absorbed radiation(8%)
Total solar heat excluded(16%)
Total solar heat admitted(84%)
Total passing heat = Passing radiation
      + Absorbed solar radiation’s internal flow
      + Conduction heat gain

## Slide 9: Solar heat gain factor
● On a given time and direction, solar heat gain per unit area and unit time through the double reinforced glass
- Penetration solar heat gain factor
- Absorption solar heat gain factor

## Slide 10: Overview of the relationship between cooling load and heat gain
Instantaneous
Heat
gain
Furnishings,
Structure,
Variable heat storage
Heat extraction
By equipment
Instantaneous
Cooling load
CLTD and CLF method
Convection component
Radiation component
Convection
(with time delay)
Swing of space temperature
Heat
rejected

## Slide 11: Light, middle, heavy structure’s real cooling load and solar heat gain
Instantaneous
heat gain
Light
Medium
Medium
Medium
Actual cooling load
Heavy
Time
Heat gain or cooling load

## Slide 12: Cooling load of forced air cooling
Cooling
coil
Return air
Exhaust
Makeup
Fan
Supply air

## Slide 13: Actual cooling load from fluorescent lights
Heat storage
Lights on
Lights off
Heat gain or cooling load
Heat storage
Stored
heat removed
Instantaneous heat gain
Actual cooling load
Cooling load
if lights remain on
Time

## Slide 14: Cooling load calculation
Heat balance method
Transfer function method
CLTD/SCL/CLF method

## Slide 15: Evolution of calculating methods

## Slide 16: 1) The heat balance method
The energy flow in each section is equilibrium. Get a solution by energy equilibrium of each space’s air separating by each wall, roof and ceiling.
= Density of air
= Specific heat of air
= Volumetric flow rate of outdoor air entering into the room at time Θ
= Outdoor air temperature at time Θ
= Ventilating air volume flow rate at time Θ
= Ventilating temperature at time Θ
= Solar heat radiation amount into the room at time Θ
= Lighting heat radiation into the room at time Θ
= Facility heat radiation into the room at time Θ

## Slide 17: 2) The transfer function method
Specification
- Time rating that relates variables of past values and others at discontinuous time interval
- Derived from response coefficient
Type
- conduction transfer function
- room transfer function

## Slide 18: Overview of transfer function
Calculate solar
Intensities for
each hour for
each exterior
surface
Calculate transmitted
Solar heat gain factors
Calculate absorbed
Solar heat gain factors
Calculate solar
Temperatures for
each hour for each
Exterior surface
Using”solar” WF coe-
Fficients and transmitted
Solar heat gains,
calculate hourly cooling
loads due to
transmitted solar heat gain
Using “conduction”WF
Coefficients and sum of
Conduction heat gains
And window conduction
Heat gains, calculate
Hourly cooling loads
Due to conduction heat
gain, Absorbed solar heat
Gains and window
Conduction heat gains
Calculate infiltration
loads
Using “lighting”WF
Coefficient and lighting
Heat gains, calculate
Hourly cooling loads
Due to lighting
Using “occupant/equipment”
WF coefficients and sum of
Occupant heat gains and
Equipment heat gains,
Calculate hourly cooling loads
Due to occupants and equipment
Characterize
Effects of
Control system
Calculate transmitted
Solar heat gain for each
Hour of each window
Calculate absorbed
Solar heat gain for each
hour for each window
Using CTF, calculate
Conduction heat gain
For each hour for each
Exterior surface and any
Thermally massive interior
Surfaces separating
Different temperature
needs
Calculate conduction
Heat gain for each hour
For each window
Determine lighting
Heat gains
Determine occupant
Heat gains
Determine equipment
Heat gains
If desired,
correct
Cooling loads
For effects of
Control system
and temperature
With space
air transfer
functions

## Slide 19: Order of transfer function calculation
Cooling
Load
Interior
Heat
Gain
Exterior
Heat
Gain

## Slide 20
3) CLTD/SCL/CLF Method
Cooling Load Temperature Difference
: Temperature difference of cooling load of
the ceiling, wall and glass (exterior cooling load)
A : Area of the ceiling, wall and glass
calculated by floor plan drawing (㎡)
U : Total heat transfer coefficient of
the ceiling, wall and glass
CLTD

## Slide 21: Following CLTD example’s conditions are given below. All conditions are steady-state. Outdoor temperature 35℃(95 F) Indoor temperature 26℃ (78 F) Maximum temperature range 12℃ (21 F)
Structure | Structure’s characteristic and material | CLTD value per time at July |  |  |  | 
 |  | 6 AM | 12 PM | 15 PM | 18 PM | 0 AM
Ceiling | 25mm Wood | -3 | 42 | 50 | 33 | 1
 | 50mm high-density concrete | 2 | 17 | 34 | 39 | 15
 | Steel sliding | 8 | 9 | 21 | 31 | 23
Wall (South direction) | 25mm wood | 0 | 12 | 21 | 18 | 6
 | 100mm insulator | 4 | 8 | 13 | 14 | 9
 | 300mm high-density concrete | 7 | 4 | 7 | 12 | 13

## Slide 22
Modified CLTD = CLTD + (78 – Indoor temperature)
+ (Modified outdoor temperature – 85)
※ Modified outdoor temperature
= Designed outdoor temperature – (Daily temperature range/2)
Modified CLTD
⇒ Use it if the above criteria does not fit.

## Slide 23
# Example
One-story building located in Las Vegas, Nevada has 50mm high-density concrete ceiling. Find the value of cooling load of 100 m2 at solar time 6 AM and 6 PM by CLTD method. Designed outdoor temperature is 41℃, daily temperature range is 1.11℃, designed indoor temperature is 23℃ and U = 0.07.

## Slide 24
Solution
Modified outdoor temperature = 41 – (1.11/2) = 40.445 ℃
6 AM CLTD = 7 + (26 – 23) + (40.445 – 29.44) = 21.005 ℃
6 PM CLTD = 78 + (26 - 23) + (40.445 - 29.44) = 92.005 ℃
6 AM cooling load
q = UA(CLTD) = 0.07(100)21.005 = 147.035 W
6 PM cooling load
q = UA(CLTD) = 0.07(100)92.005 = 644.035 W

## Slide 25
Shading Cooling Load
: Solar cooling load factor for the
presence or absence of internal shading
SC(Shading Coefficient) :
The ratio between
heat gain by a given lighting surface &
heat gain passing through DSA (Double
reinforced plate glass)
Outside cooling load
SCL
Solar load through glass

## Slide 26
# Shielding coefficient(SC) of insulating/insulation glass
A. Single Glass |  |  |  |  | 
Type of Glass | Nominal Thickness |  | Solar Trans.a | Shading Coefficient | 
 |  |  |  | h0 = 4.0 | h0 = 3.0
 | In. | mm |  | BTU/(hr-ft2-F) | BTU/(hr-ft2-F)
Clear | 1/8 | 3.2 | 0.86 | 1.00 | 1.00
 | 1/4 | 6.4 | 0.78 | 0.94 | 0.95
 | 3/8 | 9.5 | 0.72 | 0.90 | 0.92
 | 1/2 | 12.7 | 0.67 | 0.87 | 0.88
Heat absorbing | 1/8 | 3.2 | 0.64 | 0.83 | 0.85
 | 1/4 | 6.4 | 0.46 | 0.69 | 0.73
 | 3/8 | 9.5 | 0.33 | 0.60 | 0.64
 | 1/2 | 12.7 | 0.24 | 0.53 | 0.58
B. Insulating Glassb |  |  |  |  | 
Clear out. Clear in | 1/8c | 3.2 | 0.71e | 0.88 | 0.88
Clear out, clear in | 1/4 | 6.4 | 0.61 | 0.81 | 0.82
Heat absorbingd, clear in | 1/4 | 6.4 | 0.36 | 0.55 | 0.58
a Refer to manufacturer’s literature
b Refer to factory-assembled units or windshield chassis on basic glass by using 3/16, 1/4 or 1/2 air space
c Window thickness (Not assembled unit’s thickness)
d Refer to ray, bronze and green colored heat-absorption glass
e Transmissivity of assembled unit
Reference : ASHRAE Handbook, Fundamentals Volume, 1992.

## Slide 27
1) Human body
CLF
Cooling Load Factor
: Coefficient related to the time in the room
: Sensible heat generated by human
N : The number of people in the room

## Slide 28
Type | Continuously spending time in the room | The elapsed time after someone comes into the room or facility operates |  |  |  | 
 |  | 4 | 8 | 12 | 18 | 20
65mm concrete floor Ceiling Carpet floor Plaster wall Shielded room | 2 | 0.08 | 0.01 | 0 | 0 | 0
 | 8 | 0.95 | 0.98 | 0.04 | 0.01 | 0.01
 | 10 | 0.95 | 0.98 | 0.12 | 0.01 | 0.01
 | 16 | 0.96 | 0.99 | 0.99 | 0.12 | 0.05
65mm concrete floor Ceiling Vinyl floor Plaster wall Shielded room | 2 | 0.11 | 0.04 | 0.01 | 0 | 0
 | 8 | 0.85 | 0.95 | 0.13 | 0.03 | 0.02
 | 10 | 0.85 | 0.95 | 0.24 | 0.05 | 0.03
 | 16 | 0.87 | 0.95 | 0.98 | 0.25 | 0.15
# Example of CLF values in no heat generation by human or facility case

## Slide 29
2) Lighting
CLF : Cooling load coefficient by lighting
per unit time
W : Total generation of lighting [W]
: Lighting ratio
: Special allowable factor

## Slide 30
Type | Continuously lighting time | The elapsed time after lighting |  |  |  | 
 |  | 4 | 8 | 12 | 18 | 20
65mm concrete floor Ceiling Carpet floor Plaster wall Shielded room | 8 | 0.96 | 0.98 | 0.03 | 0.01 | 0.01
 | 10 | 0.97 | 0.98 | 0.07 | 0.02 | 0.02
 | 12 | 0.97 | 0.98 | 0.98 | 0.02 | 0.02
 | 14 | 0.97 | 0.98 | 0.99 | 0.03 | 0.03
65mm concrete floor Ceiling Vinyl floor Plaster wall Shielded room | 8 | 0.93 | 0.96 | 0.05 | 0.02 | 0.02
 | 10 | 0.93 | 0.96 | 0.13 | 0.03 | 0.03
 | 12 | 0.93 | 0.96 | 0.97 | 0.05 | 0.04
 | 14 | 0.94 | 0.97 | 0.98 | 0.07 | 0.05
# Example of CLF value by lighting

## Slide 31
3) Power equipment
CLF : Cooling load coefficient by
continuous operation time and hood
processing
: Load ratio

## Slide 32
# Example of CLF value by machine having a hood
Type | Continuously operating time | The elapsed time after operation |  |  |  | 
 |  | 4 | 8 | 12 | 18 | 20
65mm concrete floor Ceiling Carpet floor Plaster wall Shielded room | 8 | 0.93 | 0.97 | 0.06 | 0.01 | 0.01
 | 10 | 0.93 | 0.97 | 0.17 | 0.01 | 0.01
 | 12 | 0.94 | 0.97 | 0.99 | 0.03 | 0.03
 | 14 | 0.94 | 0.99 | 0.99 | 0.07 | 0.04
65mm concrete floor Ceiling Vinyl floor Plaster wall Shielded room | 8 | 0.79 | 0.93 | 0.19 | 0.04 | 0.03
 | 10 | 0.79 | 0.93 | 0.34 | 0.07 | 0.04
 | 12 | 0.8 | 0.93 | 0.97 | 0.11 | 0.07
 | 14 | 0.8 | 0.93 | 0.97 | 0.21 | 0.13

## Slide 33
# Various load ratio of cook tools
Heat Source | Cook tools | Load ratio
Electricity | Frying pot | 0.03
 | Oven | 0.07
 | Steam equipment | 0.04
Gas | Frying pot | 0.02
 | Oven | 0.08
 | Gas stove | 0.06

## Slide 34
Ex) Calculating cooling load by people (CLF method)
There is big office having 10 personal office. There are 4 people in secretary room.
And there are drawing room, waiting room, secretary office and executive office.
Find cooling load when solar time is 3 PM. 1) Assume the number of people, the room having people, time. 2) Assume a floating population 3) Decide the number of people to calculate total heat gain by consider 1) & 2)
4) Get sensible/latent heat amount by data in the table below. 5) Calculate cooling load by sum of sensible and latent heat load.
Place | Activity | Sensible Heat [Btu/hr] | Sensible Heat [W] | Latent Heat [Btu/hr] | Latent Heat [W]
Theater | Sitting | 225 | 66 | 105 | 31
Office, Home | Light working | 245 | 72 | 155 | 45
Department store, Market | Working with standing | 250 | 73 | 200 | 59
Dance Hall | Light dancing | 305 | 89 | 545 | 160
Factory | Machine work | 635 | 186 | 965 | 283
Gym | Exercising | 710 | 208 | 1090 | 320
Heat gain by people

## Slide 35
♣ Solution
Following assumption would be reasonable because there are no additional data.
- 7 people are in personal office between 8 AM to 5 PM.
- 3 secretaries and 1 guide are keeping the seat and always be there.
- 2 people are in waiting room because waiting room’s people number is very flexible.
- 1 person is in executive office.
- 1 person is in secretary office.
- Total people is 15 and every people do light work in sitting.
- One male and one female as a group.
- Because they do light work, sensible heat is 245Btu/hr and latent heat is 155Btu/hr.
In this case, sensible heat load by people is following below.
q1=15*155=2325 Btu/hr
Assume everyone eat lunch in this place. Then their whole staying time is 9 hours and 3 PM is 7th time to starting time. In this case, CLF is 0.93. Latent cooling load is following below.
q2=15*245*0.93=3418 Btu/hr
Then, total cooling load at 3 PM is following below.
q=q1+q2=2325+3418=5743 Btu/hr
Resident could go in and out by various schedule. In this case, we should calculate by each person.

## Slide 36: Ex) Load calculation of cooling warehouse
Heat intrusion through heat-resistant wall
Q : Heat intrusion [kcal/h]
U : Total heat transfer coefficient [kcal/㎡h℃]
A : Wall area [㎡]
Δt : Temperature difference between outdoor and indoor air [℃]
Q = UAΔt

## Slide 37
2) Heat intrusion by ventilation
Q = EVn/24
Q : Calories intrude by ventilation [kcal/h]
E : Ventilation calories per unit volume
n : Number of ventilation per 24 hour
V : Effective volume [㎥]
Ventilation calories conversing graph

## Slide 38
Volume [㎥] | Number of ventilation [number/h] | Volume [㎥] | Number of ventilation [number/h]
5 | 1.9(46) | 160 | 0.27(6.5)
10 | 1.3(31) | 200 | 0.24(5.8)
15 | 1.05(25) | 250 | 0.22(5.2)
20 | 0.9(21.5) | 300 | 0.2(4.7)
30 | 0.7(16.5) | 400 | 0.18(4.2)
40 | 0.6(14) | 500 | 0.16(3.7)
50 | 0.52(12.5) | 700 | 0.13(3.0)
60 | 0.46(11) | 900 | 0.11(2.7)
80 | 0.38(9.2) | 1100 | 0.1(2.3)
100 | 0.35(8.5) | 1400 | 0.09(2.0)
120 | 0.33(7.8) | 1700 | 0.08(1.8)
140 | 0.3(7.2) | 2000 | 0.07(1.6)
The number of ventilation by refrigerator volume ( ( ) is per 24 hour )

## Slide 39
3) Cooling calories of goods
Q : Cooling calories of goods (Sensible heat) [kcal/h]
G : Incoming amount per 1 day [kg/24h]
c : Specific heat of goods
Δt : Maximum temperature difference between input goods and indoor air [℃]
▲ Q = GcΔt/24
▲ QL = Gr/24
QL : Cooling calories of goods (Latent heat) [kcal/h]
G : Incoming amount per 1 day
r : latent heat of goods [kcal/kg]

## Slide 40
4) Heat generation by worker
heat generation by workers are going in and out
Q = The number of workers
× Heat generation by human body
× (working time/24)

## Slide 41
Refrigerator temperature [℃] | A human body heat generation [kcal/h num] | Refrigerator temperature [℃] | A human body heat generation [kcal/h num]
10 | 180 | -15 | 315
5 | 205 | -20 | 340
0 | 235 | -25 | 370
-5 | 200 | -30 | 390
-10 | 290 | -45 | 470
Human body heat generation by refrigerator’s temperature
Area of refrigerator [㎥] | The number of workers
Below 250 ㎥ | 1
250 ~ 500 ㎥ | 2
500 ~ 750 ㎥ | 3
750 ~ 1000 ㎥ | 4
The number of workers by refrigerator’s size

## Slide 42: Ex) Calculating load of freezer
Object item
Freezing criteria
Cooling system
Insulation
Equipment capacity
Building construction
Cooling method
# 1. Design Criteria

## Slide 43
# 2. Load calculating
Power
load
calories
Freezing final drying calories
Freezing
calories
Freezing point drying calories
Total
target
object
freezing
load
Final load considering safety ratio
+
+
Heat generation during work
Workers heat generation
+
Freezing
outer heat
intrusion
Heat intrusion by ventilation

## Slide 44
Thinking
⊙ Describe the criteria to consider in the calculation of load of household refrigerator.