## Slide 1: Environmental Thermal Engineering
Lecture # 2
Min soo Kim
Mechanical & Aerospace Engineering

## Slide 2
  Carnot cycle and
  Actual vapor-compression cycle

## Slide 3: Fundamentals of cycle
Most important refrigeration cycle
(Most widely used cycle)
The vapor-compression cycle
Process
Vapor compressed
Condensed to a liquid
Pressure is dropped
Evaporate at a low pressure

## Slide 4: Fundamentals of cycle
Temperature, K
Entropy, kJ/kg·K
1
2
3
4
Carnot heat engine
Temperature, K
Entropy, kJ/kg·K
1
2
3
4
Refrigeration cycle
Carnot heat engine and refrigeration cycle

## Slide 5: Fundamentals of cycle
Compressor
Evaporator
Condenser
Turbine
1
3
4
2
Temperature, K
Entropy, kJ/kg·K
1
2
3
4
Schematic and T-S diagram of Carnot ref. cycle

## Slide 6: Fundamentals of cycle
Temperature, K
Entropy, kJ/kg·K
1
2
3
4
Processes of the Carnot refrigeration cycle
1 - 2 Adiabatic compression
2 – 3 Isothermal rejection of heat
3 – 4 Adiabatic expansion
4 – 1 Isothermal addition of heat
The reason why we discuss the Carnot cycle
The Carnot cycle serves as a standard of comparison.
The Carnot cycle provides a convenient guide to the temperatures that should be maintained to achieve maximum effectiveness

## Slide 7: COP
Coefficient of performance (1)
The concept of the performance index of the refrigeration cycle is the same as efficiency.
It represent the ratio

## Slide 8: COP
Coefficient of performance (2)
The performance term in the refrigeration cycle is called the coefficient of performance (COP) , define as,

## Slide 9: COP
Express the COP of the Carnot cycle in terms of the temperatures that exist in the cycle. We know the heat transferred in a reversible process can express T his way.
Condition for highest coefficient of performance

## Slide 10: T-S diagram analysis
Temperature, K
Entropy, kJ/kg·K
Net work
Refrigeration
2
1
3
4
This Figure can represent the amount of useful refrigeration and the net work .
T-S diagram (1)

## Slide 11: T-S diagram analysis
Useful refrigeration =
Net work =
T-S diagram (2)
The useful refrigeration and net work
Expression for COP of Carnot refrigeration cycle

## Slide 12: T-S diagram analysis
A low value of T2 will make the COP high
A high value of T1 will make the COP high
How can we achieve a highest COP in Carnot cycle?
The value of T1 has a more pronounced effect on the COP than T2, because a high value of T1 increases the numerator and decreases the denominator.

## Slide 13: T-S diagram analysis
Can we have the infinite COP as T1 is set equal to T2 ?
Temperature, K
Entropy, kJ/kg·K
Temperature limitation

## Slide 14: T-S diagram analysis
Temperature, K
Entropy, kJ/kg·K
1
3
2
4
Heat transfer
      In this heat rejection process, refrigerant must transfer its heat to somewhere.
      In this refrigeration process, refrigerant must add the heat from the cold room.
2 → 3
4 → 1

## Slide 15: T-S diagram analysis
Temperature, K
Entropy, kJ/kg·K
303.15 K
253.15 K
Example
If the refrigeration system must maintain a cold room at – 20 ℃ and can reject heat to the atmosphere at 30 ℃, how can we control the temperatures, T1 and T2?

## Slide 16: T-S diagram analysis
T1 must be higher than 303.15K.
T2 must be lower than 253.15K.
Temperature, K
Entropy, kJ/kg·K
303.15 K
253.15 K
The answer (1)

## Slide 17: T-S diagram analysis
Temperature, K
Entropy, kJ/kg·K
303.15 K
253.15 K
The answer (2)
For higher COP, we can keep the ΔT as small as possible.

## Slide 18: Overall heat transfer
q = heat, W
U = overall heat-transfer coefficient,
A = heat-transfer area,
ΔT = temperature change, K
Reduction of ΔT
Reduction of ΔT can be accomplished by increasing A or U in equation.

## Slide 19: Overall heat transfer
How to accomplish high U ?
In reality, we can make U high rather than make A high for given q, because we need to make less the space of refrigerator.
But a large heat transfer area is accomplished

## Slide 20: Overall heat transfer
We can make the air speed around heat exchanger high.
air
For a high value of U (1)

## Slide 21: Overall heat transfer
We can use the finned tube.
The low finned tube
For a high value of U (2)
Helically finned tube

## Slide 22: Overall heat transfer
The water around the heat exchanger will help the heat exchange.
water
(But it will promote to corrode the heat exchanger.)
For a high value of U (3)

## Slide 23
Revision of the Carnot cycle

## Slide 24: Compression process
Temperature, K
Entropy, kJ/kg·K
1
4
3
2
1 → 2

## Slide 25: Compression process
Wet compression
compression with liquid droplet
Dry compression
compression with no droplet of liquid
Two kinds of compression

## Slide 26: Compression process
Liquid refrigerant may be trapped in the head of the cylinder by the rising piston, possibly damaging the valve or the cylinder head.
High-speed compressor are susceptible to damage by liquid because of the short time available for heat transfer.
The droplet of liquid may wash the lubricating oil from the walls of the cylinder, accelerating wear.
Problem of wet compression

## Slide 27: Revision of the Carnot cycle
If the refrigerant entering compressor is saturated vapor, the compression from point 1 to 2 is called dry compression.
Temperature, K
Entropy, kJ/kg·K
1
4
3
2
Superheat horn
Dry compression

## Slide 28: Revision of the Carnot cycle
Superheat horn
On the temperature-entropy diagram superheat horn represent the additional work for dry compression.
Temperature, K
Entropy, kJ/kg·K
1
4
3
2
Superheat horn

## Slide 29: Expansion process
Temperature, K
Entropy, kJ/kg·K
1
4
3
2
3 → 4

## Slide 30: Another revision in expansion process
The possible work that can be derived from the engine is a small fraction of that which must be supplied to the compressor.
Practical difficulties such as lubrication intrude when a fluid of two phases drives the engine.
The economics of the power recovery have in the past not justified the cost of the expansion engine.
The practical difficulties in expansion engine (1)

## Slide 31: Expansion process
The practical difficulties in expansion engine (2)
But the possibility of using an expansion engine should continue to be studied as the energy cost increases.

## Slide 32: Expansion process
Expansion valve
Throttling device
Because necessity still remains of reducing the pressure in the expansion process we can use throttling device such as a valve.

## Slide 33: Expansion process
Throttling happens in expansion device such as an expansion valve.
No changes in potential and kinetic energy and with no heat loss, h3 = h4; that is, the process is isenthalpic.
The constant-enthalpy throttling process is irreversible, and during the process the entropy increases.
Isenthalpic process

## Slide 34: Expansion process
Throttling process
The throttling process take place 3 → 4 in this figure.
Temperature, K
Entropy, kJ/kg·K
1
4
3
2

## Slide 35
Standard vapor-compression cycle

## Slide 36: Standard vapor-compression cycle
Compression process
1-2 process
Reversible and adiabatic compression from saturated vapor to the condenser pressure
Temperature, K
Entropy, kJ/kg·K
1
4
3
2

## Slide 37: Standard vapor-compression cycle
Condensation process
2-3 process
Reversible rejection heat at constant pressure, causing de-superheating and condensation of the refrigerant.
Temperature, K
Entropy, kJ/kg·K
1
4
3
2

## Slide 38: Standard vapor-compression cycle
Expansion process
3-4 process
Irreversible expansion at constant enthalpy from saturated liquid to the evaporator pressure
Temperature, K
Entropy, kJ/kg·K
1
4
3
2

## Slide 39: Standard vapor-compression cycle
Evaporation process
4-1 process
Reversible addition of heat at constant pressure causing evaporation to saturated vapor
Temperature, K
Entropy, kJ/kg·K
1
4
3
2

## Slide 40: Standard vapor-compression cycle
Pressure, kPa
Enthalpy, kJ/kg
Critical point
t= constant
= constant
s = constant
Saturated-vapor line
Saturated-liquid line
P - h diagram of refrigerant
The pressure- enthalpy diagram is the usual graphic means of presenting refrigerant properties.

## Slide 41: Standard vapor-compression cycle
The actual p-h diagram of R22

## Slide 42: Standard vapor-compression cycle
Pressure, kPa
Enthalpy, kJ/kg
Condensation
Evaporation
Compression
Expansion
4
3
2
1
Cycle on the pressure-enthalpy diagram
In refrigeration practice, the enthalpy is one of the most important properties sought, and the pressure can usually be determined most easily.

## Slide 43: Standard vapor-compression cycle
The work of compression
= h2 – h1
The refrigerating effect
= h1 – h4
COP
Condensation
Evaporation
Compression
Expansion
4
3
2
1
Pressure, kPa
Enthalpy, kJ/kg

## Slide 44
Liquid line – suction line
heat exchange

## Slide 45: Liquid line – suction line heat exchange
LLSL-HX
Liquid line – suction line heat exchange cycle
Normal cycle

## Slide 46: Liquid line – suction line heat exchange
Pressure, kPa
Enthalpy, kJ/kg
4
3
2
1
5
6
2
4
1
2
3
4
5
6
Schematic and graph

## Slide 47: Liquid line – suction line heat exchange
Superheating of the vapor leaving the evaporator
Subcooling of the liquid leaving the condenser
Increased the refrigeration effect
( h = refrigeration effect )
Advantage

## Slide 48: Liquid line – suction line heat exchange
Increase compressor work
Pressure, kPa
Enthalpy, kJ/kg
4
3
2
1
5
6
2’
4’
Disadvantage
Additional cost of heat exchanger

## Slide 49
Actual vapor-compression cycle

## Slide 50: Actual vapor-compression cycle
Pressure ,kPa
Enthalpy, kJ/kg
4
3
2
1
Subcooling
Pressure drop
Superheating
Pressure drop
Pressure drop in the compressor and evaporator
Superheating of the vapor leaving the evaporator
Subcooling of the liquid leaving the condenser
The compression is not isentropic.
( There are inefficiencies due to friction and other losses. )

## Slide 51: HW #2
When the efficiency of refrigerating systems in household(for example, refrigerator, air conditioner, etc.) operate in an ideal state, let’s consider about how much energy customer could save.