## Slide 1: Environmental Thermal Engineering
Lecture # 6
Min soo Kim
Mechanical & Aerospace Engineering

## Slide 2
  The principle and application of absorption refrigerating system

## Slide 3: Background
Global environmental pollution problem
Restrict usage of Freon gases ( CFC and HCFC)
R11 – Prohibition of production in 1994
R22 – Expected to abolish all in 2020
Necessity enlargement for air-conditioning using non- Freon gas
Absorption refrigerating system :
- using natural coolant such as water or ammonia
- operates with gases, wasted heat or solar heat

## Slide 4: Background
An Energy policy of Korea
Reduce the amount of use of energy
Develop substitute Energy for Petroleum
For diversity of importation of energy,
government introduce LNG and
Flame type air conditioners
Stabilization of electricity supplying system in summer
Standardization of gas accommodation
Standardization of demand of electricity in different season

## Slide 5: History of absorption refrigerating machine
1859’ & 1860’ –patent for absorption refrigerating system using NH3/H2O F by Fredinand Carr,
1913’ – Theoretical establishment about absorption refrigerating system by 독 by E. Altenkirch, German
1920’ – patent for absorption refrigerating system without circulation pump by introducing hydrogen by G. Munters and B. Conplaten, Switzerland.
Early 1940’ – Develop H2O/LiBr system by W.H. Carrier.
1955’ – 550 USRT, H2O/LiBr system
1960’ – 660 USRT, H2O/LiBr system
1968’ – Develop direct heating type, double effect absorption refrigerating machine, Japan
In Korea, we produce absorption refrigerating system after 1984’.

## Slide 6: Absorption refrigerating system
Former vapor compression refrigerant system
Using electricity for compression
Electricity ifs advanced energy
Demand large amount of energy for vapor compression for large change of specific volume
The way to increase pressure of coolant by reducing power consumption
: vapor compression process ⇒ liquid compression process

## Slide 7: Vapor compression vs Liquid compression
1
2
P
h
4
4'
3
Ex) Coolant : Ammonia
Evaporator - 0℉, 30.42 psi
Condenser - 90℉, 180.73 psi
Vapor compression process h3 = 1422 kJ/kg h4,isen = 1684 kJ/kg
Wisen = 262 kJ/kg NH3
Liquid compression process (water is slovent) Concentration of Ammonia(x) = 0.4, Specific volume of solution(v) = 0.001149
W = ΔP*v/x = 2.98 kJ/kg NH3

## Slide 8: Absorption refrigerating system
Condenser
Evaporator
Generator
Absorber
Refrig. vapor
Exp. Valve A
Exp. Valve B
Weak solution
Strong solution
Refrigerant only
Refrigerant plus absorbant
Pump

## Slide 9: Components
Absorber It absolves evaporated refrigerant steam in evaporator and sends regenerator.
Regenerator It absolves coolant and heats solution from absorber, so it separates coolant and absorbent. Evaporated coolant is sanded to condenser and absorbent is sanded to absorber.
Condenser It condenses refrigerant steam by heat exchanging with cooling water.
Evaporator It sprays liquid coolant from condenser on upper part of cooling pipe. Depriving the heat, this liquid is evaporated and sanded to absorber.

## Slide 10: Flow of energy
Absorption fluids system
Generator heating medium
Pump
Refrigerated space
Environment
External energy transfer for absorption refrigerating system

## Slide 11: Absorption refrigerating cycle
Evaporator
Absorber
Regenerator
Condenser
Heating
Thin solution
Condensed solution
Refrigerant steam
Refrigerant steam
Single effect absorption refrigerating cycle

## Slide 12: Absorption refrigerating cycle
A absorption refrigerating cycle having 2 regenerator changing thin solution to condensed solution
Double effect absorption refrigerating cycle

## Slide 13: Coolant and absorber for absorption refrigerating system
large latent heat, high critical pressure
Difference of the boiling point between absorber and coolant is large and small heat capacity
The freezing point of coolant and absorber is low and coolant does not coagulation at operation stop.
No corrosiveness to ion and pipe material, and needs stability to heat.
Cheap and easily purchase.
Requirements of coolant and absorber

## Slide 14: Coolant and absorber for absorption refrigerating system
A binary system based on H2O/LiBr, and a advanced ternary and quaternary system.
Water has large evaporative latent heat, and high COP and easily acquire.
Due to large boiling point, it is hard to air cooling.
It cannot acquire cold heat source below 0℃.
Due to strong corrosiveness, it is hard to manage solution.
Recently, water receives attention as coolant/absorber of absorption refrigerating system for solar heat.
A system using Water as coolant (H2O/LiBr)

## Slide 15: Coolant and absorber for absorption refrigerating system
Due to high operating pressure, it needs pressure vessel.
Ammonia has adequate characteristic for coolant.
Toxicity, flammable and explosiveness is critical defects.
Applications : large absorption refrigerating system for industry, small absorption refrigerant system for air conditioning.
A system using Ammonia as coolant (NH3/H2O)

## Slide 16: Coolant and absorber for absorption refrigerating system
larger latent heat and low freezing point compared to water.
flammable problem.
CF3CH2OH receives attention for substitutes of H2O/LiBr
Dimethly formamide solition (DMF) is largely used for absorbent.
R21, R22, R124, R31, R123, R133a are coolants for this system.
A system using Alcohol as coolant
A system using Halocarbon as coolant

## Slide 17: Coolant and absorber for absorption refrigerating system
Coolant | Absorbent
Water type H2O | LiBr, LiI, LiSCN, LiCl, NaOH, CsBr, CsF, RbF LiBRLiSCN, LiBr-ZnCl2, LiBr-ZnBr2, LiBr-C4H6O2, LiBr-C2H6O2, LiBr-LiCl, LiCl-CaCl2-Zn(NO3)2, CH3OH-LiBr-ZnCl2
Ammonia type NH3, CH3NH2, C2H5NH2 | H2O,H2O, LiSCN, C2H6O, LiSCN-NaSCN, H2O
Alcohol type CH3OH, C2H5OH, CFH2CH2OH, CF2HCH2OH, CClF2CH2OH, CF3CH2CH2OH, CF3CH2OH | LiBr, LiI, ZnBr2, LiBr-ZnCl2, LiI-ZnBr2 TEGDME, N-methyle-2-pirolidone
Halocarbon type R22, R21, R124, R23, R31, R123, R133 | TEGDME, TrEGDME, DMF DMA, DEGDME, DMF DMA, DEGDME, ETFE, BTFE
Combination of coolant and absorbent

## Slide 18
Process of cycle

## Slide 19: Basic process of thermodynamics
Superheat region
Subcooled liquid region
Temperature
x
Condensing line
Boiling line
T-x diagram of isotropic 2-fluids mixture
isotropic 2-fluids mixture
Uniform composition
It does not separated by mechanical ways
It needs pressure, temperature and concentration
Several saturated temperature in each pressure

## Slide 20: h(i)-x Diagram
h(i)-x diagram of isotropic 2-fluids mixture in liquid-gas region

## Slide 21: H2O/NH3 h(i)-x diagram (1)

## Slide 22: H2O/NH3 h(i)-x diagram (2)

## Slide 23: H2O/NH3 h(i)-x diagram (3)

## Slide 24: LiBr/H2O h(i)-x diagram

## Slide 25: Adiabatic mixing
①
②
③
x1
x3
x2
i1
i2
i3

## Slide 26: Example of adiabatic mixing
① P = 150 psi T = 220F x = 0.25 m = 20 lbm/min
② P = 150 psi T = 100F Saturated solution m = 10 lbm/min
Concentration
Enthalpy
1
2
3
150 psi
150 psi
0.25
0.41
0.72
180F
Equilibrium construction line
③ point 3 is saturation condition. To calculate temperature, apply graphical method using equilibrium line.
f
g

## Slide 27: Heating and cooling process
To increase purity
in water-Ammonia system
Concentration
Enthalpy
1
2
3
4
5
6
7

## Slide 28: Throttling process
①
②
Concentration
Enthalpy
1
2
f
P1
g
P2
P2
t1
t2
① : High pressure, saturated solution
② : low pressure, saturated condition Temperature of final state can be calculated applying graphical method.

## Slide 29: Calculation of heat in absorption refrigerating cycle
Condenser
Evaporator
Generator
Absorber
Refrig. vapor
Exp. Valve A
Exp. Valve B
Weak solution
Strong solution
Pump

## Slide 30: COP is ideal system

## Slide 31
Kind of systems

## Slide 32: Absorption refrigerating system (1)
1800’ - the oldest absorption refrigerating cycle started f fff from middle of 1800s
1960’ – after 1960, it utilized for residential air-conditioning a applications
Coolant – Ammonia, Absorption - water
Water and Ammonia are flammable both, and have similar boiling point -> It need to separate H2O from generator
Generator is composed with generator, rectification column and shunt.
Water-Ammonia Absorption refrigerating system

## Slide 33: Absorption refrigerating system (2)
Fig. Water-Ammonia Absorption refrigerating system for industry
Condenser
Evaporator
Absorber
Generator
Dephlegmtor
Pump
Water-Ammonia Absorption refrigerating system for industry

## Slide 34: Absorption refrigerating system (3)
Gen 1
Gen 2
Absorber 1
Absorber 2
Sol. HX1
Sol. HX2
Precooler
Condenser
Rectifier 1
Rectifier 2
Fig. 2단 이중효용 Water-Ammonia Absorption refrigerating system
Double effect Water-Ammonia Absorption refrigerating system

## Slide 35: Absorption refrigerating system (4)
Pure water 40℃
Water vapor p=7.38 kPa
LiBr-H2O 80℃,59%
80℃
30℃
40℃
10℃
50
59
7.38 kPa
1.23 kPa
Water vapor p=7.38 kPa
LiBr-H2O Absorption refrigerating system

## Slide 36: Absorption refrigerating system (4)
LiBr-H2O Absorption refrigerating system

## Slide 37: Absorption refrigerating system (4)
LiBr-H2O Absorption refrigerating system
Fig. Example of LiBr-H2O Absorption refrigerating system

## Slide 38
Classification of systems

## Slide 39: Classification of absorption type
Type | Absorption refrigerating system | Absorption chilling system | Absorption heat pump system
Function | Cold water (4~15℃) | Cold water (4~15℃) hot water (40~80℃) | hot water (50~104℃) Steam (140℃~)
Heat sources | Steam , hot water | Exhausted gas Combustion gas | Steam, combustion heat, wasted hot water
Application | cooling, cooling process | Cooling/heating | 

## Slide 40: Characteristics of absorption type
 | Absorption chilling system | Absorption refrigerating system | Turbo refrigerating system
Driving source | Heat from gas combustion | Steam, hot water | Electricity
Components | Evaporator, absorber, condenser, regenerator, heat exchanger, combustion room, circulation pump | Evaporator, absorber, condenser, regenerator, heat exchanger, combustion room, circulation pump | Evaporator, condenser, compressor , oil cooler
operating pressure | Vacuum | Vacuum | Condenser : above atmospheric pressure Evaporator : varies according to coolant
heating method | Hot water | Boiler | Boiler or heat pump
vibration and noise | Low noise | Low noise | High noise

## Slide 41: Absorption refrigerating system
Device acquiring cold water about 4~15℃
Cooling only
Generally, temperature at cold water outlet is 7℃, and difference between inlet and outlet is 5℃.
Driving method | Condition of standard heat source |  | Main purpose
 | Single effect | Double effect | 
Steam type | 1.0 ~ 1.5 kg/cm2 steam |  | Hospital, factory
Hot water type | 140℃ hot water | 200℃ hot water | District cooling
Warm water type | 80℃ warm water |  | Solar heat cooling, Cooling through wasted heat

## Slide 42
BCD100S ~ BCD1650S...(100R/T ~ 1650R/T)

## Slide 43: Absorption chilling system
Driving force is heat energy from combustion of LPG and gas
Heat source equipment producing hot and cold water simultaneously.
Mainly flame and absorption type chillers
Condition for cold water : 12 ~7℃
Condition for warm water : 50 ~ 60℃

## Slide 44: Absorption chilling system
Classification of Absorption chilling system by capacity
Size | Small | Medium | Large
Refrigerating capacity | ~ 40RT | 40~100RT | 100RT ~
Combustion heat | ~150,000 kcal/h | 150,000~300,000 kcal/h | 300,000 kcal/h~
Figure | Outdoor with case | Outdoor, indoor | Indoor
Combustion control | On/off or 3-way | 3-way or proportion | proportion
Bleeding device | Non-condensable gas Tank + Paratium | Vacuum pump method | Non-condensable gas Tank Vacuum pump method
Coolant circulation method | Natural circulation Air lift pump | Coolant pump | Coolant pump
Electric facilities | Cooling tower, water pump, coolant, electric facility | electric facility | 

## Slide 45: Absorption refrigerating system
Heating and cooling
Cooling cycle
Heating cycle

## Slide 46: Problems (1)
What is the COP of an ideal heat-operated refrigeration system that has a source temperature of heat of 100℃, a refrigerating temperature of 5℃, and an ambient temperature of 30℃?
Problems

## Slide 47: Problems (2)
water vapor
LiBr-water solution
100℃
Condenser
Evaporator
Generator
Absorber
40℃
10℃
30℃
Compute the flow rate of refrigerant (water) through the condenser and evaporator in the cycle shown in below figure if the pump delivers 0.6 kg/s and the following temperature prevail: generator, 100℃; condenser, 40℃; evaporator, 10℃; and absorber, 30℃
0.6 kg/s
①
②
③
④
⑤

## Slide 48: Problems (2)
100℃
30℃
40℃
10℃
50
66.4
7.38 kPa
1.23 kPa
High pressure – generator, condenser
Low pressure – absorber, evaporator

## Slide 49: Problems (2)
w1 = 0.6 kg/s, w2 = 0.452 kg/s, w3 = w4 = w5 = 0.148 kg/s
x1 = 50%, x2 = 66.4 %
45%
50%
55%
-180
-160
25℃
30℃
h1 ( h at 30℃ & x = 0.5 )= -168 kJ/kg
h2 ( h at 100℃ & x = 0.664 )= -52 kJ/kg
h3 ( h of saturated vapor at 100℃ )= 2676 kJ/kg
h4 ( h of saturated liquid at 40℃ )= 167.5 kJ/kg
h5 ( h of saturated vapor at 10℃ )= 2520 kJ/kg
Compute heat inputs, outputs and the COP

## Slide 50: Problems (3)
Absorption cycle with heat exchanger
Condenser
Evaporator
Generator
Absorber
water vapor
LiBr-water solution
100℃
40℃
10℃
30℃
①
②
③
④
⑤
⑥
⑦
52℃
w1 = 0.6 kg/s

## Slide 51: Problems (3)
w1 = w2 =0.6 kg/s, w3 = w4 = 0.452 kg/s, w5 = w6 = w7 = 0.148 kg/s
x1 = 50%, x2 = 66.4 %
h1 = -168 kJ/kg
h3 = -52 kJ/kg
h5 = 2676 kJ/kg
h6 = 167.5 kJ/kg
h7 = 2520 kJ/kg
h2 = h at 52℃ & x 0.5 = -120 kJ/kg
qhx = w1(h2-h1)=28.8 kW
h4 = -116 kJ/kg

## Slide 52: Absorption refrigerating system in # 301
Left-side

## Slide 53: Absorption refrigerating system in # 301
Right-side

## Slide 54: Absorption refrigerating system in # 301
Upper-front

## Slide 55: Absorption refrigerating system in # 301
Schematic diagram for driving Absorption refrigerating system